# SELNIKEL INDUSTRIAL BOILER COMMISSIONING GUIDE

Site Installation, Electrical Verification & Regulatory Standards | Revision: REV-01

## 1. Pre-Commissioning Electrical Limits

| Terminal | Signal Type | Allowed Range |
| --- | --- | --- |
| L1-L2-L3 | Main Power | 380 - 420 V |
| P1-P2 | Pressure 4-20 mA | 0.0 - 25.0 bar |

## 2. Standards, Directives & Regulatory Compliance

All Selnikel industrial steam boilers and burner installations strictly comply with mandatory European harmonized standards:

Shell Boilers Manufacturing Standard: EN 12953 for shell boilers design, safety and manufacturing requirements.

Pressure Equipment Directive: PED 2014/68/EU Category IV conformity module H1 certification.

Forced Draught Gas Burner Standard: EN 676 automatic forced draught burners for gaseous fuels.

## 3. Flue Gas Emission Limits

| Emission Parameter | Natural Gas Limit | Light Oil Limit |
| --- | --- | --- |
| CO Concentration | < 50 mg/Nm³ | < 80 mg/Nm³ |
| NOx Class III | < 100 mg/kWh | < 150 mg/kWh |