# SELNIKEL MONOBLOCK INDUSTRIAL BURNERS

Service & Maintenance Operations Manual | Document ID: MB-OM-2026 | Revision: REV-01

## 1. Technical Air & Combustion Data

The combustion air blower operates at a nominal rotational speed of 2850 rpm with static air pressure of 45 mbar. Optimum flue gas O2 content must be maintained between 3.0% and 3.5%.

## 2. Periodic Maintenance Schedule & Intervals

Regular maintenance ensures emission compliance and prevents nozzle clogging:

| Component | Inspection Action | Service Interval | Torque / Spec |
| --- | --- | --- | --- |
| Burner Nozzles | Clean and inspect spray pattern | 500 hour | 25 Nm |
| Ignition Electrodes | Check spark gap (3.0 mm) | 1000 hour | 3.0 mm gap |
| Flame Sensor Photocell | Clean optical glass surface | 1000 hour | Clean room spec |
| Gas Valve Train | Tightness and leak test | 6 month | No bubble at 100 mbar |
| Complete Blower Overhaul | Bearing lubrication and dynamic balancing | 1 year | ISO 1940 G2.5 |